## gen
| name | bus | p | max_p | min_p | vm | scaling | in_service | type | current_source
0 | Kotu 4 | Double Busbar 2 | 5 | 5 | 0 | 1.03 | 1 | TRUE | HFO | TRUE
3 | Kotu 7 | Double Busbar 2 | 4.8 | 4.8 | 0 | 1.03 | 1 | TRUE | HFO | TRUE

## mv_line
| line_name | from_bus | to_bus | length | std_type | parallel
0 | MV Line 1 | Bus SB1 | Bus MV0 | 0.22 | 243-AL1/39-ST1A 20.0 | 1
1 | MV Line 2 | Bus SB1 | Bus MV1 | 20.93 | 94-AL1/15-ST1A 20.0 | 2
2 | MV Line 3 | Bus MV1 | Bus MV2 | 17.05 | 94-AL1/15-ST1A 20.0 | 1
3 | MV Line 4 | Bus SB1 | Bus MV3 | 7.43 | 94-AL1/15-ST1A 20.0 | 2
4 | MV Line 5 | Bus SB1 | Bus MV4 | 0.36 | 243-AL1/39-ST1A 20.0 | 2
5 | MV Line 6 | Bus MV3 | Bus MV5 | 7.6 | 94-AL1/15-ST1A 20.0 | 1
6 | MV Line 7 | Bus MV5 | Bus MV6 | 3.3 | 94-AL1/15-ST1A 20.0 | 1

## hv_line
| line_name | from_bus | to_bus | length | std_type | parallel
0 | HV Line 1 | Bus HV 0 | Bus HV 1 | 10 | 149-AL1/24-ST1A 20.0 | 1
1 | HV Line 2 | Bus HV 1 | Bus HV 2 | 15 | 149-AL1/24-ST1A 20.0 | 1
2 | HV Line 3 | Bus HV 1 | Bus HV 3 | 61 | 149-AL1/24-ST1A 20.0 | 1
3 | HV Line 4 | Bus SB2 | Bus HV 2 | 4 | 149-AL1/24-ST1A 20.0 | 2
4 | HV Line 5 | Bus HV 2 | Bus HV 4 | 36 | 149-AL1/24-ST1A 20.0 | 1
5 | HV Line 6 | Bus HV 2 | Bus SB2 | 0.5 | 149-AL1/24-ST1A 20.0 | 2
6 | HV Line 7 | Bus HV 4 | Bus HV 5 | 9 | 149-AL1/24-ST1A 20.0 | 1
7 | HV Line 8 | Bus HV 3 | Bus HV 6 | 5 | 149-AL1/24-ST1A 20.0 | 1
8 | HV Line 9 | Bus HV 5 | Bus HV 6 | 10 | 149-AL1/24-ST1A 20.0 | 1
9 | HV Line 10 | Bus HV 3 | Bus HV 7 | 13 | 149-AL1/24-ST1A 20.0 | 1
10 | HV Line 11 | Bus HV 1 | Bus HV 7 | 4 | 149-AL1/24-ST1A 20.0 | 1
11 | HV Line 12 | Bus SB2 | Bus HV 7 | 22 | 149-AL1/24-ST1A 20.0 | 1
12 | HV Line 13 | Bus SB2 | Bus HV 8 | 30 | 149-AL1/24-ST1A 20.0 | 1

## gen2
| name | bus | p | max_p | min_p | vm | scaling | in_service | type | current_source
1 | Brikama I 1 | Double Busbar 3 | 4.89 | 4.89 | 0 | 1.03 | 1 | TRUE | HFO | TRUE
2 | Brikama I 4 | Double Busbar 3 | 5 | 5 | 0 | 1.03 | 1 | TRUE | HFO | TRUE
3 | Brikama I 7 | Double Busbar 3 | 4.89 | 4.89 | 0 | 1.03 | 1 | TRUE | HFO | TRUE
4 | Brikama II 1 | Double Busbar 3 | 8 | 8 | 0 | 1.03 | 1 | TRUE | HFO | TRUE
5 | Brikama III | Double Busbar 3 | 18.4 | 18.4 | 0 | 1.03 | 1 | TRUE | HFO | TRUE

## mv_load
| load_name | bus | p_old | q | p | p2 | p3
0 | Buffer zone FJKNDA | Bus MV8 | 0.1 | 0.47 | 0.21773 | 0.18547 | 0.17136
1 | Buffer zone Ahmadiyya | Bus MV8 | 1.4 | 0.27 | 3.0482 | 2.5966 | 2.399
2 | Buffer zone Tallinding | Bus MV8 | 3.31 | 0.67 | 7.2068 | 6.1391 | 5.672
3 | Wellingara Airport | Bus MV1 | 5.7 | 0.92 | 12.4105 | 10.5719 | 9.7676
4 | Wellingara Jola Kunda | Bus MV1 | 2.7 | 0.29 | 5.8787 | 5.0078 | 4.6267
5 | BIJ Brusubi | Bus MV7 | 1.089 | 0.558 | 2.3711 | 2.0198 | 1.8661
6 | BIJ Borehole | Bus MV7 | 2.738 | 0.557 | 5.9614 | 5.0782 | 4.6919
7 | BIJ Bijilo | Bus MV7 | 0.61 | 0.123 | 1.3281 | 1.1314 | 1.0453
8 | BIJ Tranquil | Bus MV7 | 2.156 | 0.438 | 4.6942 | 3.9988 | 3.6945
9 | MD Airport | Bus MV2 | 1.71 | 1.7 | 3.7232 | 3.1716 | 2.9303
10 | MD Brikama | Bus MV2 | 2.38 | 0.64 | 5.1819 | 4.4142 | 4.0784
11 | M2 A Circuit | Bus MV5 | 1.83 | 1.14 | 3.9844 | 3.3941 | 3.1359
12 | M2 GHS | Bus MV5 | 0.83 | -1.53 | 1.8071 | 1.5394 | 1.4223
13 | M2 Marina | Bus MV5 | 3.45 | -2.32 | 7.5116 | 6.3988 | 5.9119
14 | M5 Banjul | Bus MV3 | 0.17 | 0.22 | 0.37014 | 0.3153 | 0.29131
15 | M5 Kanifing | Bus MV3 | 1.29 | 0.74 | 2.8087 | 2.3926 | 2.2106
16 | M5 Bakau | Bus MV3 | 0.64 | 0.15 | 1.3935 | 1.187 | 1.0967
17 | Feeder 1 | Bus SB1 | 3.4 | 1.04 | 7.4028 | 6.3061 | 5.8263
18 | Feeder 2 | Bus SB1 | 2.8 | 1.1 | 6.0964 | 5.1932 | 4.7981
19 | Feeder 3 | Bus SB1 | 2.49 | 0.74 | 5.4214 | 4.6183 | 4.2669
20 | Feeder 4 | Bus SB1 | 3.96 | 0.91 | 8.6221 | 7.3447 | 6.7859
21 | Feeder 5 | Bus SB1 | 2 | 0.71 | 4.3546 | 3.7095 | 3.4272
22 | Gungur | Bus MV9 | 1.1 | 0.21 | 2.395 | 2.0402 | 1.885
23 | Western Region | Bus MV9 | 1.75 | 1.61 | 3.8103 | 3.2458 | 2.9988

## Elec_Gam
Electricity demand forecast | [14 empty] | Capital expenditure for each plant |  |  |  |  | Fixed operation and maintenance cost | [8 empty] | Short run Marginal cost | [7 empty] | Generator run-time (2021)
Power plant | unit | 2021 | 2022 | 2023 | 2024 | 2025 | [8 empty] | Power plant | Status | Unit | Amount |  | Power plant | Status | Unit | 2021 | 2022 | 2023 | 2024 | 2025 |  | Power plant | Status | Unit | 2021 | 2022 | 2023 | 2024 | 2025 | Power plant | Power(MW) | Energy(MWh) | Run time(h) | Marginal cost(US$/MW) | Installed generator capacities
Peak GBA | MW | 107.76 | 126.99 | 136.25 | 146 | 157.45 | [8 empty] | Brikama I 1 | Existing NAWEC Thermal - GBA | mUS$ | 0 |  | Brikama I 1 | Existing NAWEC Thermal - GBA | mUS$ | 5e-05 | 5e-05 | 5e-05 | 0 | 0 |  | Brikama I 1 | Existing NAWEC Thermal - GBA | US$/MWh | 133.06 | 135.34 | 137.71 | 140.07 | 142.52 | Brikama I 1 | 5.5 | 5730 | 1041.8182 | 0.12772 | Power plant | Unit | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | [29 empty] | transmission line expansion
[15 empty] | Brikama I 3 | Existing NAWEC Thermal - GBA | mUS$ | 0 |  | Brikama I 3 | Existing NAWEC Thermal - GBA | mUS$ | 5e-05 | 5e-05 | 5e-05 | 0 | 0 |  | Brikama I 3 | Existing NAWEC Thermal - GBA | US$/MWh | 133.06 | 135.34 | 137.71 | 140.07 | 142.52 | Brikama I 3 | 5.5 | 5370 | 976.3636 | 0.13628 | Brikama I 1 | MW | 5.5 | 5.5 | 5.5 | 5.5 | 0 | 0 | [18 empty] | Sub-sation Name | Transformer size (kV) |  |  | New projects | Commission year | Unit | Capacity | Location | Plant type | Transmission expansion projects | Comission year | Unit | Capacity | Location
| Electricity base demand | [13 empty] | Brikama I 4 | Existing NAWEC Thermal - GBA | mUS$ | 0 |  | Brikama I 4 | Existing NAWEC Thermal - GBA | mUS$ | 5e-05 | 5e-05 | 5e-05 | 0 | 0 |  | Brikama I 4 | Existing NAWEC Thermal - GBA | US$/MWh | 138.49 | 140.85 | 143.3 | 145.75 | 148.29 | Brikama I 4 | 5.5 | 40 | 7.2727 | 19.0424 | Brikama I 3 | MW | 5.5 | 5.5 | 5.5 | 5.5 | 0 | 0 | [19 empty] | Sub-station | Feeder | 1 | Brikama III | 2021 | MW | 18.4 | Brikama Power Station | HFO Thermal Plant | Jabang - Brikama | 2025 | kV | 225 | Jabang - Brikama
Power plant | unit | 2021 | 2022 | 2023 | 2024 | 2025 | [8 empty] | Brikama I 5 | Existing NAWEC Thermal - GBA | mUS$ | 0 |  | Brikama I 5 | Existing NAWEC Thermal - GBA | mUS$ | 5e-05 | 5e-05 | 5e-05 | 0 | 0 |  | Brikama I 5 | Existing NAWEC Thermal - GBA | US$/MWh | 127.49 | 129.62 | 131.84 | 134.06 | 136.36 | Brikama I 5 | 5.5 | 13340 | 2425.4545 | 0.052563 | Brikama I 4 | MW | 5.5 | 5.5 | 5.5 | 5.5 | 0 | 0 | [17 empty] | 1 | Kotu dispatch | 33 | 11 | 2 | ICE | 2022 | MW | 30 | Kotu Power station | HFO Thermal Plant | Brikama - Kaolack | 2025 | kV | 225
Base GBA | MW | 92.36 | 108.29 | 120.71 | 131.76 | 137.95 | [8 empty] | Brikama I 7 | Existing NAWEC Thermal - GBA | mUS$ | 0 |  | Brikama I 7 | Existing NAWEC Thermal - GBA | mUS$ | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 |  | Brikama I 7 | Existing NAWEC Thermal - GBA | US$/MWh | 134.06 | 136.34 | 138.71 | 141.07 | 143.52 | Brikama I 7 | 5.5 | 3250 | 590.9091 | 0.22687 | Brikama I 5 | MW | 5.5 | 5.5 | 5.5 | 5.5 | 0 | 0 | MW | KARPOWER |  | TOTAL | KOTU |  |  |  |  | BRIKAMA 1 |  |  |  |  | BRIKAMA 2 | TOTAL | OVERALL | 2 | Wellingara | 33 | 11 | 3 | Imports PPA | 2022 | MW | 40 | Guinea | Hydro power | New jabang sub-station | 2025 | kV | 225 | Jabang
[15 empty] | Brikama II 1 | Existing NAWEC Thermal - GBA | mUS$ | 0 |  | Brikama II 1 | Existing NAWEC Thermal - GBA | mUS$ | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 |  | Brikama II 1 | Existing NAWEC Thermal - GBA | US$/MWh | 111.72 | 113.63 | 115.62 | 117.6 | 119.66 | Brikama II 1 | 8.5 | 53610 | 6307.0588 | 0.017713 | Brikama I 7 | MW | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | [17 empty] | 3 | Medina | 33 | 11 | 4 | World Bank Jambur Solar | 2022 | MW | 20 | Jambur | Solar plant | New brimaka sub-station | 2025 | kV | 225 | Brikama
[15 empty] | Kotu 4 | Existing NAWEC Thermal - GBA | mUS$ | 0 |  | Kotu 4 | Existing NAWEC Thermal - GBA | mUS$ | 1e-05 | 1e-05 | 0 | 0 | 0 |  | Kotu 4 | Existing NAWEC Thermal - GBA | US$/MWh | 127.19 | 129.4 | 131.69 | 133.98 | 136.35 | Kotu 4 | 5.5 | 20230 | 3678.1818 | 0.03458 | Brikama II 1 | MW | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 |  | G1 | G2 |  | G4 | G5 | G6 | G7 | G8 | G1 | G3 | G4 | G5 | G7 | G1 |  |  | 4 | Bufferzone | 33 | 11 | 5 | Battery storage | 2022 | MWh | 6 | Jambur | Lithium batteries | New kotu sub-station | 2025 | kV | 225 | Kotu
| Electricity low demand | [13 empty] | Kotu 5 | Existing NAWEC Thermal - GBA | mUS$ | 0 |  | Kotu 5 | Existing NAWEC Thermal - GBA | mUS$ | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 |  | Kotu 5 | Existing NAWEC Thermal - GBA | US$/MWh | 124.32 | 126.46 | 128.67 | 130.88 | 133.18 | Kotu 5 | 11 | 55920 | 5083.6364 | 0.024455 | Kotu 4 | MW | 5.5 | 5.5 | 5.5 | 0 | 0 | 0 | Installed Capacity | 15 | 15 | 30 | 5.5 | 11 | 5 | 5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 8.5 | 68 | 98 | 5 | Mile 2 | 33 | 11 | 6 | CCGT Cote d'Ivoire | 2023 | MW | 40 | Cote d'Ivoire | CCGT
Power plant | unit | 2021 | 2022 | 2023 | 2024 | 2025 | [8 empty] | Kotu 6 | Existing NAWEC Thermal - GBA | mUS$ | 0 |  | Kotu 6 | Existing NAWEC Thermal - GBA | mUS$ | 1e-05 | 1e-05 | 0 | 0 | 0 |  | Kotu 6 | Existing NAWEC Thermal - GBA | US$/MWh | 128.54 | 130.75 | 133.05 | 135.34 | 137.72 | Kotu 6 | 5 | 7310 | 1462 | 0.087921 | Kotu 5 | MW | 11 | 11 | 11 | 11 | 11 | 11 | peak generation level ( 9/12/2020) | 15 | 15 | 30 | 5 | 0 | 0 | 4.8 | 0 | 4.89 | 0 | 5 | 0 | 4.89 | 8 | 32.58 | 62.58 | 6 | Mile 5 | 33 | 11 | 7 | CCGT Senegal | 2024 | MW | 60 | Senegal | CCGT
Base GBA | MW | 84.71 | 95.63 | 97.11 | 102.77 | 105.42 | [8 empty] | Kotu 7 | Existing NAWEC Thermal - GBA | mUS$ | 0 |  | Kotu 7 | Existing NAWEC Thermal - GBA | mUS$ | 5e-05 | 5e-05 | 5e-05 | 0 | 0 |  | Kotu 7 | Existing NAWEC Thermal - GBA | US$/MWh | 136.64 | 138.84 | 141.11 | 143.39 | 145.76 | Kotu 7 | 5 | 330 | 66 | 2.0703 | Kotu 6 | MW | 5 | 5 | 5 | 0 | 0 | 0 | [17 empty] | 7 | Bijilo | 33 | 11
[15 empty] | Kotu 8 | Existing NAWEC Thermal - GBA | mUS$ | 0 |  | Kotu 8 | Existing NAWEC Thermal - GBA | mUS$ | 5e-05 | 5e-05 | 5e-05 | 6e-05 | 5e-05 |  | Kotu 8 | Existing NAWEC Thermal - GBA | US$/MWh | 143.14 | 145.54 | 148.02 | 150.5 | 153.08 | Kotu 8 | 5.5 | 20 | 3.6364 | 39.3635 | Kotu 7 | MW | 5 | 5 | 5 | 5 | 0 | 0 | [17 empty] | 8 | Brikama | 33 | 11
[15 empty] | Karpower | Existing rented - GBA | mUS$ | 0 |  | Karpower | Existing rented - GBA | mUS$ | 0 | 0 | 0 | 0 | 0 |  | Karpower | Existing rented - GBA | US$/MWh | 121.62 | 123.9 | 126.28 | 128.66 | 131.12 | Karpower | 30 | 249160 | 8305.3333 | 0.014644 | Kotu 8 | MW | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
[15 empty] | Brikama III | Committed | mUS$ | 18.7 |  | Brikama III | Committed | mUS$ | 0.00013 | 0.00013 | 0.00013 | 0.00013 | 0.00013 |  | Brikama III | Committed | US$/MWh | 111.72 | 113.63 | 115.62 | 117.6 | 119.66 | Brikama III | 18.4 | 116050 | 6307.0652 | 0.017713 | Karpower | MW | 30 | 30 | 0 | 0 | 0 | 0
[42 empty] | Brikama III | MW | 0 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4
[42 empty] | ICE 30 MW (HFO) | MW | 0 | 0 | 30 | 30 | 30 | 30
[42 empty] | Imports PPA (Guinea Hydro) | MW | 0 | 0 | 40 | 40 | 40 | 40
[42 empty] | World Bank - Jambur Solar PV | MW | 0 | 0 | 20 | 20 | 20 | 20
[42 empty] | World Bank Jambur Battery | MW | 0 | 0 | 6 | 6 | 6 | 6
[42 empty] | Total | MW | 98 | 116.4 | 182.4 | 171.9 | 144.9 | 144.9
[15 empty] | Emission Quantity | [8 empty] | Total Fuel cost
[15 empty] | Power plant | Status | Unit | 2020 | 2022 | 2023 | 2024 | 2025 |  | Fuel Name | Unit | 2021 | 2022 | 2023 | 2024 | 2025
[15 empty] | System | Emission | tonne | 424131.54 | 362952.27 | 322066.74 | 331311.5 | 340563.19 |  | HFO | US$ | 68579.02 | 58168.18 | 4820.63 | 7141.18 | 7141.18
[24 empty] | LFO | US$ | 48.55 | 69.64 | 0 | 0 | 0
Generator run-time (2021) | [7 empty] | Short run Marginal cost
Power plant | Capacity (MW) | Energy(MWh) | Run time(h) | Marginal cost(US$/MW) | Marginal cost (€/MW) |  |  | Power plant | Status | Unit | 2021 | 2022 | 2023 | 2024 | 2025
Brikama I 1 | 5.5 | 5730 | 1041.8182 | 0.12772 | 0.10856 |  |  | Brikama I 1 | Existing NAWEC Thermal - GBA | US$/MWh | 133.06 | 135.34 | 137.71 | 140.07 | 142.52
Brikama I 4 | 5.5 | 40 | 7.2727 | 18.975 | 16.1288 |  |  | Brikama I 4 | Existing NAWEC Thermal - GBA | US$/MWh | 138 | 140.85 | 143.3 | 145.75 | 148.29
Brikama I 7 | 5.5 | 3250 | 590.9091 | 0.22677 | 0.19275 |  |  | Brikama I 7 | Existing NAWEC Thermal - GBA | US$/MWh | 134 | 136.34 | 138.71 | 141.07 | 143.52
Brikama II 1 | 8.5 | 53610 | 6307.0588 | 0.017758 | 0.015094 |  |  | Brikama II 1 | Existing NAWEC Thermal - GBA | US$/MWh | 112 | 113.63 | 115.62 | 117.6 | 119.66
Kotu 4 | 5.5 | 33910 | 6165.4545 | 0.020599 | 0.017509 |  |  | Kotu 4 | Existing NAWEC Thermal - GBA | US$/MWh | 127 | 129.4 | 131.69 | 133.98 | 136.35
Kotu 7 | 5 | 330 | 66 | 2.0758 | 1.7644 |  |  | Kotu 7 | Existing NAWEC Thermal - GBA | US$/MWh | 137 | 138.84 | 141.11 | 143.39 | 145.76
Karpower | 30 | 249160 | 8305.3333 | 0.014689 | 0.012486 |  |  | Karpower | Existing rented - GBA | US$/MWh | 122 | 123.9 | 126.28 | 128.66 | 131.12
Brikama III | 18.4 | 116050 | 6307.0652 | 0.017758 | 0.015094 |  |  | Brikama III | Committed | US$/MWh | 112 | 113.63 | 115.62 | 117.6 | 119.66
ICE | 0 | 0 | 0 | 0 | 0 |  |  | ICE | Comitted | US$/MWh | 0 | 134.56 | 137.01 | 139.47 | 142.02
Jambur Solar | 0 | 0 | 0 | 0 | 0 |  |  | Jambur Solar | Comitted | US$/MWh | 0 | 0 | 0 | 0 | 0
Hydro-Imports | 0 | 0 | 0 | 0 | 0 |  |  | Hydro-Imports | Comitted | US$/MWh | 0 | 108.7 | 110.4 | 112.1 | 113.9
Short run Marginal cost
[7 empty] | Power plant | Status | Unit | 2021 | 2022 | 2023 | 2024 | 2025
[7 empty] | Brikama I 1 | Existing NAWEC Thermal - GBA | €/MW | 0.10856 | 1.1504 | 1.1705 | 0 | 0
[7 empty] | Brikama I 4 | Existing NAWEC Thermal - GBA | €/MW | 16.1288 | 16.4618 | 16.7482 | 0 | 0
[7 empty] | Brikama I 7 | Existing NAWEC Thermal - GBA | €/MW | 0.19275 | 31.8695 | 32.4235 | 32.9751 | 33.5478
[7 empty] | Brikama II 1 | Existing NAWEC Thermal - GBA | €/MW | 0.015094 | 0.015314 | 0.043622 | 0.067476 | 0.083692
[7 empty] | Kotu 4 | Existing NAWEC Thermal - GBA | €/MW | 0.017509 | 0.01784 | 0 | 0 | 0
[7 empty] | Kotu 7 | Existing NAWEC Thermal - GBA | €/MW | 1.7644 | 59.007 | 59.9718 | 0 | 0
[7 empty] | Karpower | Existing rented - GBA | €/MW | 0.012486 | 0 | 0 | 0 | 0
[7 empty] | Brikama III | Committed | €/MW | 0.015094 | 0.015314 | 0.015582 | 0.066801 | 0.083177
[7 empty] | ICE | Comitted | €/MW | 0 | 0.12338 | 349.3755 | 349.3755 | 362.151
[7 empty] | Jambur Solar | Comitted | €/MW | 0 | 0 | 0 | 0 | 0
[7 empty] | Hydro-Imports | Comitted | €/MW | 0 | 0.027682 | 0.41476 | 0.61737 | 2.7081

## lv_lines (hidden)
| line_name | from_bus | to_bus | length | std_type
0 | LV Line1.1 | Bus LV0 | Bus LV1.1 | 0.08 | NAYY 4x120 SE
1 | LV Line1.2 | Bus LV1.1 | Bus LV1.2 | 0.08 | NAYY 4x120 SE
2 | LV Line1.3 | Bus LV1.2 | Bus LV1.3 | 0.08 | NAYY 4x120 SE
3 | LV Line1.4 | Bus LV1.3 | Bus LV1.4 | 0.08 | NAYY 4x120 SE
4 | LV Line1.5 | Bus LV1.4 | Bus LV1.5 | 0.08 | NAYY 4x120 SE
5 | LV Line2.1 | Bus LV0 | Bus LV2.1 | 0.12 | NAYY 4x120 SE
6 | LV Line2.2 | Bus LV2.1 | Bus LV2.2 | 0.12 | NAYY 4x120 SE
7 | LV Line2.3 | Bus LV2.2 | Bus LV2.3 | 0.12 | NAYY 4x120 SE
8 | LV Line2.4 | Bus LV2.3 | Bus LV2.4 | 0.12 | NAYY 4x120 SE
9 | LV Line2.2.1 | Bus LV2.2 | Bus LV2.2.1 | 0.12 | NAYY 4x120 SE
10 | LV Line2.2.2 | Bus LV2.2.1 | Bus LV2.2.2 | 0.12 | NAYY 4x120 SE