## gen
| name | bus | p | max_p | min_p | vm | scaling | in_service | type | current_source
0 | Kotu 4 | Double Busbar 2 | 5 | 5 | 0 | 1.03 | 1 | TRUE | HFO | TRUE
1 | Kotu 7 | Double Busbar 2 | 4.8 | 4.8 | 0 | 1.03 | 1 | TRUE | HFO | TRUE

## mv_line
| line_name | from_bus | to_bus | length | std_type | parallel
0 | MV Line 1 | Bus SB1 | Bus MV0 | 0.22 | 243-AL1/39-ST1A 20.0 | 1
1 | MV Line 2 | Bus SB1 | Bus MV1 | 20.93 | 94-AL1/15-ST1A 20.0 | 2
2 | MV Line 3 | Bus MV1 | Bus MV2 | 17.05 | 94-AL1/15-ST1A 20.0 | 1
3 | MV Line 4 | Bus SB1 | Bus MV3 | 7.43 | 94-AL1/15-ST1A 20.0 | 2
4 | MV Line 5 | Bus SB1 | Bus MV4 | 0.36 | 243-AL1/39-ST1A 20.0 | 2
5 | MV Line 6 | Bus MV3 | Bus MV5 | 7.6 | 94-AL1/15-ST1A 20.0 | 1
6 | MV Line 7 | Bus MV5 | Bus MV6 | 3.3 | 94-AL1/15-ST1A 20.0 | 1

## hv_line
| line_name | from_bus | to_bus | length | std_type | parallel
0 | HV Line 1 | Bus HV 0 | Bus HV 1 | 10 | 149-AL1/24-ST1A 20.0 | 1
1 | HV Line 2 | Bus HV 1 | Bus HV 2 | 15 | 149-AL1/24-ST1A 20.0 | 1
2 | HV Line 3 | Bus HV 1 | Bus HV 3 | 61 | 149-AL1/24-ST1A 20.0 | 1
3 | HV Line 4 | Bus SB2 | Bus HV 2 | 4 | 149-AL1/24-ST1A 20.0 | 2
4 | HV Line 5 | Bus HV 2 | Bus HV 4 | 36 | 149-AL1/24-ST1A 20.0 | 1
5 | HV Line 6 | Bus HV 2 | Bus SB2 | 0.5 | 149-AL1/24-ST1A 20.0 | 2
6 | HV Line 7 | Bus HV 4 | Bus HV 5 | 9 | 149-AL1/24-ST1A 20.0 | 1
7 | HV Line 8 | Bus HV 3 | Bus HV 6 | 5 | 149-AL1/24-ST1A 20.0 | 1
8 | HV Line 9 | Bus HV 5 | Bus HV 6 | 10 | 149-AL1/24-ST1A 20.0 | 1
9 | HV Line 10 | Bus HV 3 | Bus HV 7 | 13 | 149-AL1/24-ST1A 20.0 | 1
10 | HV Line 11 | Bus HV 1 | Bus HV 7 | 4 | 149-AL1/24-ST1A 20.0 | 1
11 | HV Line 12 | Bus SB2 | Bus HV 7 | 22 | 149-AL1/24-ST1A 20.0 | 1
12 | HV Line 13 | Bus SB2 | Bus HV 8 | 30 | 149-AL1/24-ST1A 20.0 | 1
13 | Wellingara-Jabang | Bus HV 1 | Bus HV 9 | 8 | 149-AL1/24-ST1A 20.0 | 1
14 | Jambur-Medina | Bus HV 2 | Bus HV 10 | 3 | 94-AL1/15-ST1A 20.0 | 1
15 | Soma-Bijilo | Bus HV 11 | Bus HV 4 | 128 | 149-AL1/24-ST1A 20.0 | 1
16 | Soma-Bufferzone | Bus HV 11 | Bus HV 7 | 250 | 149-AL1/24-ST1A 20.0 | 1
17 | Soma-Medina | Bus HV 11 | Bus HV 2 | 142 | 149-AL1/24-ST1A 20.0 | 1

## gen2
| name | bus | p | max_p | min_p | vm | scaling | in_service | type | current_source
0 | Brikama I 1 | Double Busbar 3 | 4.89 | 4.89 | 0 | 1.03 | 1 | TRUE | HFO | TRUE
1 | Brikama I 4 | Double Busbar 3 | 5 | 5 | 0 | 1.03 | 1 | TRUE | HFO | TRUE
2 | Brikama I 7 | Double Busbar 3 | 4.89 | 4.89 | 0 | 1.03 | 1 | TRUE | HFO | TRUE
3 | Brikama II 1 | Double Busbar 3 | 8 | 8 | 0 | 1.03 | 1 | TRUE | HFO | TRUE
4 | Brikama III | Double Busbar 3 | 18.4 | 18.4 | 0 | 1.03 | 1 | TRUE | HFO | TRUE

## hv_load
| load_name | bus | p1 | p2 | p | q
0 | F1 | Bus SB2 | 6.333 | 5.333 | 3.667 | 1.1
1 | F2 | Bus SB2 | 6.333 | 5.333 | 3.667 | 1.1
2 | F3 | Bus SB2 | 6.333 | 5.333 | 3.667 | 1.1

## mv_load
| load_name | bus | p1 | q | p2 | p
0 | Buffer zone FJKNDA | Bus MV8 | 0.21773 | 0.47 | 0.18547 | 0.17136
1 | Buffer zone Ahmadiyya | Bus MV8 | 3.0482 | 0.27 | 2.5966 | 2.399
2 | Buffer zone Tallinding | Bus MV8 | 7.2068 | 0.67 | 6.1391 | 5.672
3 | Wellingara Airport | Bus MV1 | 12.4105 | 0.92 | 10.5719 | 9.7676
4 | Wellingara Jola Kunda | Bus MV1 | 5.8787 | 0.29 | 5.0078 | 4.6267
5 | BIJ Brusubi | Bus MV7 | 2.3711 | 0.558 | 2.0198 | 1.8661
6 | BIJ Borehole | Bus MV7 | 5.9614 | 0.557 | 5.0782 | 4.6919
7 | BIJ Bijilo | Bus MV7 | 1.3281 | 0.123 | 1.1314 | 1.0453
8 | BIJ Tranquil | Bus MV7 | 4.6942 | 0.438 | 3.9988 | 3.6945
9 | MD Airport | Bus MV2 | 3.7232 | 1.7 | 3.1716 | 2.9303
10 | MD Brikama | Bus MV2 | 5.1819 | 0.64 | 4.4142 | 4.0784
11 | M2 A Circuit | Bus MV5 | 3.9844 | 1.14 | 3.3941 | 3.1359
12 | M2 GHS | Bus MV5 | 1.8071 | -1.53 | 1.5394 | 1.4223
13 | M2 Marina | Bus MV5 | 7.5116 | -2.32 | 6.3988 | 5.9119
14 | M5 Banjul | Bus MV3 | 0.37014 | 0.22 | 0.3153 | 0.29131
15 | M5 Kanifing | Bus MV3 | 2.8087 | 0.74 | 2.3926 | 2.2106
16 | M5 Bakau | Bus MV3 | 1.3935 | 0.15 | 1.187 | 1.0967
17 | Feeder 1 | Bus SB1 | 7.4028 | 1.04 | 6.3061 | 5.8263
18 | Feeder 2 | Bus SB1 | 6.0964 | 1.1 | 5.1932 | 4.7981
19 | Feeder 3 | Bus SB1 | 5.4214 | 0.74 | 4.6183 | 4.2669
20 | Feeder 4 | Bus SB1 | 8.6221 | 0.91 | 7.3447 | 6.7859
21 | Feeder 5 | Bus SB1 | 4.3546 | 0.71 | 3.7095 | 3.4272
22 | Gungur | Bus MV9 | 2.395 | 0.21 | 2.0402 | 1.885
23 | Western Region | Bus MV9 | 3.8103 | 1.61 | 3.2458 | 2.9988

## s_gens
| name | bus | p | q | sn | scaling | in_service | type | current_source
0 | Solar Park | Bus HV 10 | 20 |  |  | 1 | TRUE | SGEN | TRUE
1 | Hydro-power (import) | Bus VH 2 | 40 |  |  | 1 | TRUE | SGEN | TRUE

## 225_kV_line
| line_name | from_bus | to_bus | length | std_type | parallel
0 | Jabang-Brikama line | Bus VH 0 | Bus VH 1 | 15 | 243-AL1/39-ST1A 110.0 | 1
1 | Jabang-Kotu line | Bus VH 1 | Bus VH 3 | 17 | 243-AL1/39-ST1A 110.0 | 1
2 | Kotu-Kaolack line | Bus VH 3 | Bus VH 4 | 28.8 | 243-AL1/39-ST1A 110.0 | 1
3 | Jabang-OMVG line | Bus VH 1 | Bus VH 2 | 22 | 243-AL1/39-ST1A 110.0 | 1
5 | Brikama-Kotu line | Bus VH 0 | Bus VH 3 | 32 | 243-AL1/39-ST1A 110.0 | 1
6 | Kotu-OMVG line | Bus VH 3 | Bus VH 2 | 39 | 243-AL1/39-ST1A 110.0 | 1

## Elec_Gam
Electricity demand forecast | [14 empty] | Capital expenditure for each plant |  |  |  |  | Fixed operation and maintenance cost
Power plant | unit | 2021 | 2022 | 2023 | 2024 | 2025 |  |  | Electricity low demand | [5 empty] | Power plant | Status | Unit | Amount |  | Power plant | Status | Unit | 2021 | 2022 | 2023 | 2024 | 2025 |  |  |  | Installed generator capacities
Peak GBA | MW | 107.76 | 126.99 | 136.25 | 146 | 157.45 |  | Power plant | unit | 2021 | 2022 | 2023 | 2024 | 2025 | Brikama I 1 | Existing NAWEC Thermal - GBA | mUS$ | 0 |  | Brikama I 1 | Existing NAWEC Thermal - GBA | mUS$ | 5e-05 | 5e-05 | 5e-05 | 0 | 0 |  |  |  | Power plant | Unit | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | [29 empty] | transmission line expansion | [6 empty] | load_name | bus | 2022 | 2023 | 2024 | 2025
[8 empty] | Base GBA | MW | 84.71 | 95.63 | 97.11 | 102.77 | 105.42 | Brikama I 3 | Existing NAWEC Thermal - GBA | mUS$ | 0 |  | Brikama I 3 | Existing NAWEC Thermal - GBA | mUS$ | 5e-05 | 5e-05 | 5e-05 | 0 | 0 |  |  |  | Brikama I 1 | MW | 5.5 | 5.5 | 5.5 | 5.5 | 0 | 0 | [18 empty] | Sub-sation Name | Transformer size (kV) |  |  | New projects | Commission year | Unit | Capacity | Location | Plant type | Transmission and sub-station expansion projects | Comission year | Unit | Capacity | New feeder | Comission year | Location | Capacity (kV) |  |  | p | P | P
| Electricity base demand | [13 empty] | Brikama I 4 | Existing NAWEC Thermal - GBA | mUS$ | 0 |  | Brikama I 4 | Existing NAWEC Thermal - GBA | mUS$ | 5e-05 | 5e-05 | 5e-05 | 0 | 0 |  |  |  | Brikama I 3 | MW | 5.5 | 5.5 | 5.5 | 5.5 | 0 | 0 | [19 empty] | Sub-station | Feeder | 1 | Brikama III | 2021 | MW | 18.4 | Brikama Power Station | HFO Thermal Plant | New Jabang sub-station | 2025 | kV | 225 | F1 | 2022 | Brikama | 33 | Buffer zone FJKNDA | Bus MV8 | 0.18547 | 0.18547 | 0.18547 | 0.18547
Power plant | unit | 2021 | 2022 | 2023 | 2024 | 2025 | [8 empty] | Brikama I 5 | Existing NAWEC Thermal - GBA | mUS$ | 0 |  | Brikama I 5 | Existing NAWEC Thermal - GBA | mUS$ | 5e-05 | 5e-05 | 5e-05 | 0 | 0 |  |  |  | Brikama I 4 | MW | 5.5 | 5.5 | 5.5 | 5.5 | 0 | 0 | [17 empty] | 1 | Kotu dispatch | 33 | 11 | 2 | ICE | 2022 | MW | 30 | Kotu Power station | HFO Thermal Plant | New Brimaka sub-station | 2025 | kV | 225 | F2 | 1905-07-14 | Brikama | 33 | Buffer zone Ahmadiyya | Bus MV8 | 2.5966 | 2.5966 | 2.5966 | 2.5966
Base GBA | MW | 92.36 | 108.29 | 120.71 | 131.76 | 137.95 | [8 empty] | Brikama I 7 | Existing NAWEC Thermal - GBA | mUS$ | 0 |  | Brikama I 7 | Existing NAWEC Thermal - GBA | mUS$ | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 |  |  |  | Brikama I 5 | MW | 5.5 | 5.5 | 5.5 | 5.5 | 0 | 0 | MW | KARPOWER |  | TOTAL | KOTU |  |  |  |  | BRIKAMA 1 |  |  |  |  | BRIKAMA 2 | TOTAL | OVERALL | 2 | Wellingara | 33 | 11 | 3 | Imports PPA | 2022 | MW | 40 | Guinea | Hydro power | New Kotu sub-station | 2025 | kV | 225 | F3 | 2022 | Brikama | 33 | Buffer zone Tallinding | Bus MV8 | 6.1391 | 6.1391 | 6.1391 | 6.1391
[15 empty] | Brikama II 1 | Existing NAWEC Thermal - GBA | mUS$ | 0 |  | Brikama II 1 | Existing NAWEC Thermal - GBA | mUS$ | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 |  |  |  | Brikama I 7 | MW | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | [17 empty] | 3 | Medina | 33 | 11 | 4 | World Bank Jambur Solar | 2022 | MW | 20 | Jambur | Solar plant | Jabang-Brikama line | 2025 | kV | 225 |  |  |  |  | Wellingara Airport | Bus MV1 | 10.5719 | 10.5719 | 10.5719 | 10.5719
[15 empty] | Kotu 4 | Existing NAWEC Thermal - GBA | mUS$ | 0 |  | Kotu 4 | Existing NAWEC Thermal - GBA | mUS$ | 1e-05 | 1e-05 | 0 | 0 | 0 |  |  |  | Brikama II 1 | MW | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 |  | G1 | G2 |  | G4 | G5 | G6 | G7 | G8 | G1 | G3 | G4 | G5 | G7 | G1 |  |  | 4 | Bufferzone | 33 | 11 | 5 | Battery storage | 2022 | MWh | 6 | Jambur | Lithium batteries | Jabang-Kotu line | 2025 | kV | 225 |  |  |  |  | Wellingara Jola Kunda | Bus MV1 | 5.0078 | 5.0078 | 5.0078 | 5.0078
| Uniy | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | [7 empty] | Kotu 5 | Existing NAWEC Thermal - GBA | mUS$ | 0 |  | Kotu 5 | Existing NAWEC Thermal - GBA | mUS$ | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 |  |  |  | Kotu 4 | MW | 5.5 | 5.5 | 5.5 | 0 | 0 | 0 | Installed Capacity | 15 | 15 | 30 | 5.5 | 11 | 5 | 5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 8.5 | 68 | 98 | 5 | Mile 2 | 33 | 11 | [7 empty] | Wellingara-Jabang line | 2025 | kV | 33 |  |  |  |  | BIJ Brusubi | Bus MV7 | 2.0198 | 2.0198 | 2.0198 | 2.0198
Total installed capacity | MW | 98 | 116.4 | 182.4 | 171.9 | 144.9 | 144.9 | [7 empty] | Kotu 6 | Existing NAWEC Thermal - GBA | mUS$ | 0 |  | Kotu 6 | Existing NAWEC Thermal - GBA | mUS$ | 1e-05 | 1e-05 | 0 | 0 | 0 |  |  |  | Kotu 5 | MW | 11 | 11 | 11 | 11 | 11 | 11 | peak generation level ( 9/12/2020) | 15 | 15 | 30 | 5 | 0 | 0 | 4.8 | 0 | 4.89 | 0 | 5 | 0 | 4.89 | 8 | 32.58 | 62.58 | 6 | Mile 5 | 33 | 11 | [7 empty] | Kotu-Kaolack line | 2025 | kV | 225 |  |  |  |  | BIJ Borehole | Bus MV7 | 5.0782 | 5.0782 | 5.0782 | 5.0782
Peak generation level | MW | 62.58 | UNKNOWN | UNKNOWN | UNKNOWN | UNKNOWN | UNKNOWN | [7 empty] | Kotu 7 | Existing NAWEC Thermal - GBA | mUS$ | 0 |  | Kotu 7 | Existing NAWEC Thermal - GBA | mUS$ | 5e-05 | 5e-05 | 5e-05 | 0 | 0 |  |  |  | Kotu 6 | MW | 5 | 5 | 5 | 0 | 0 | 0 | [17 empty] | 7 | Bijilo | 33 | 11 | [7 empty] | Jabang-OMVG line | 2025 | kV | 225 |  |  |  |  | BIJ Bijilo | Bus MV7 | 1.1314 | 1.1314 | 1.1314 | 1.1314
Peak supply to the load | MW | 49.603 | UNKNOWN | UNKNOWN | UNKNOWN | UNKNOWN | UNKNOWN | [7 empty] | Kotu 8 | Existing NAWEC Thermal - GBA | mUS$ | 0 |  | Kotu 8 | Existing NAWEC Thermal - GBA | mUS$ | 5e-05 | 5e-05 | 5e-05 | 6e-05 | 5e-05 |  |  |  | Kotu 7 | MW | 5 | 5 | 5 | 5 | 0 | 0 | [17 empty] | 8 | Brikama | 33 | 11 | [7 empty] | Medina-Jambur line | 2022 | kV | 33 |  |  |  |  | BIJ Tranquil | Bus MV7 | 3.9988 | 3.9988 | 3.9988 | 3.9988
Peak load demand | MW | 90.39 | 107.76 | 126.99 | 136.25 | 146 | 157.45 | [7 empty] | Karpower | Existing rented - GBA | mUS$ | 0 |  | Karpower | Existing rented - GBA | mUS$ | 0 | 0 | 0 | 0 | 0 |  |  |  | Kotu 8 | MW | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | [28 empty] | Brikama-Kotu line | 2025 | kV | 225 |  |  |  |  | MD Airport | Bus MV2 | 3.1716 | 3.1716 | 3.1716 | 3.1716
Supply-demand gap | MW | -40.787 | 8.64 | 55.41 | 35.65 | -1.1 | -12.55 | [7 empty] | Brikama III | Committed | mUS$ | 18.7 |  | Brikama III | Committed | mUS$ | 0.00013 | 0.00013 | 0.00013 | 0.00013 | 0.00013 |  |  |  | Karpower | MW | 30 | 30 | 0 | 0 | 0 | 0 | [28 empty] | Kotu-OMVG line | 2025 | kV | 225 |  |  |  |  | MD Brikama | Bus MV2 | 4.4142 | 4.4142 | 4.4142 | 4.4142
T&D line losses | % | 20.7367 | UNKNOWN | UNKNOWN | UNKNOWN | UNKNOWN | UNKNOWN | [23 empty] | Brikama III | MW | 0 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | [36 empty] | M2 A Circuit | Bus MV5 | 3.3941 | 3.3941 | 3.3941 | 3.3941
Generation losses | % | 36.1429 | UNKNOWN | UNKNOWN | UNKNOWN | UNKNOWN | UNKNOWN | [23 empty] | ICE 30 MW (HFO) | MW | 0 | 0 | 30 | 30 | 30 | 30 | [36 empty] | M2 GHS | Bus MV5 | 1.5394 | 1.5394 | 1.5394 | 1.5394
[31 empty] | Imports PPA (Guinea Hydro) | MW | 0 | 0 | 40 | 40 | 40 | 40 | [36 empty] | M2 Marina | Bus MV5 | 6.3988 | 6.3988 | 6.3988 | 6.3988
[31 empty] | World Bank - Jambur Solar PV | MW | 0 | 0 | 20 | 20 | 20 | 20 | [36 empty] | M5 Banjul | Bus MV3 | 0.3153 | 0.3153 | 0.3153 | 0.3153
[31 empty] | World Bank Jambur Battery | MW | 0 | 0 | 6 | 6 | 6 | 6 | [36 empty] | M5 Kanifing | Bus MV3 | 2.3926 | 2.3926 | 2.3926 | 2.3926
[31 empty] | Total | MW | 98 | 116.4 | 182.4 | 171.9 | 144.9 | 144.9 | [36 empty] | M5 Bakau | Bus MV3 | 1.187 | 1.187 | 1.187 | 1.187
[75 empty] | Feeder 1 | Bus SB1 | 6.3061 | 6.3061 | 6.3061 | 6.3061
Variable cost | [14 empty] | Emission Quantity | [8 empty] | Total Fuel cost | [50 empty] | Feeder 2 | Bus SB1 | 5.1932 | 5.1932 | 5.1932 | 5.1932
Power plant | Status | Unit | 2021 | 2022 | 2023 | 2024 | [6 empty] | 2025 |  | Power plant | Status | Unit | 2020 | 2022 | 2023 | 2024 | 2025 |  | Fuel Name | Unit | 2021 | 2022 | 2023 | 2024 | 2025 | [44 empty] | Feeder 3 | Bus SB1 | 4.6183 | 4.6183 | 4.6183 | 4.6183
Brikama I 1 | Existing NAWEC Thermal - GBA | mUS$ | 0.76311 | 0.07472 | 0 | 0 | [6 empty] | 0 |  | System | Emission | tonne | 424131.54 | 362952.27 | 322066.74 | 331311.5 | 340563.19 |  | HFO | US$ | 68579.02 | 58168.18 | 4820.63 | 7141.18 | 7141.18 | [44 empty] | Feeder 4 | Bus SB1 | 7.3447 | 7.3447 | 7.3447 | 7.3447
Brikama I 3 | Existing NAWEC Thermal - GBA | mUS$ | 0.71396 | 0.0461 | 0 | 0 | [6 empty] | 0 | [10 empty] | LFO | US$ | 48.55 | 69.64 | 0 | 0 | 0 | [44 empty] | Feeder 5 | Bus SB1 | 3.7095 | 3.7095 | 3.7095 | 3.7095
Brikama I 4 | Existing NAWEC Thermal - GBA | mUS$ | 0.00497 | 0.00057 | 0 | 0 | [6 empty] | 0 | [61 empty] | Gungur | Bus MV9 | 2.0402 | 2.0402 | 2.0402 | 2.0402
Brikama I 5 | Existing NAWEC Thermal - GBA | mUS$ | 1.7011 | 3.5783 | 0.86658 | 0 | [6 empty] | 0 | [61 empty] | Western Region | Bus MV9 | 3.2458 | 3.2458 | 3.2458 | 3.2458
Brikama I 7 | Existing NAWEC Thermal - GBA | mUS$ | 0.43637 | 0.00205 | 0 | 0 | [6 empty] | 0 | [61 empty] | F1 | Bus SB2 | 5.333 | 9.67 | 13.33 | 15.33
Brikama II 1 | Existing NAWEC Thermal - GBA | mUS$ | 5.9892 | 6.0918 | 2.214 | 1.4558 | [6 empty] | 1.236 | [61 empty] | F2 | Bus SB2 | 5.333 | 9.67 | 13.33 | 15.33
Kotu 4 | Existing NAWEC Thermal - GBA | mUS$ | 2.5726 | 4.3883 | 0 | 0 | [6 empty] | 0 | [61 empty] | F3 | Bus SB2 | 5.333 | 9.67 | 13.33 | 15.33
Kotu 5 | Existing NAWEC Thermal - GBA | mUS$ | 6.9522 | 8.94 | 1.828 | 1.3553 | [6 empty] | 1.0437
Kotu 6 | Existing NAWEC Thermal - GBA | mUS$ | 0.93924 | 2.8505 | 0 | 0 | [6 empty] | 0
Kotu 7 | Existing NAWEC Thermal - GBA | mUS$ | 0.04528 | 0.00146 | 0 | 0 | [6 empty] | 0
Kotu 8 | Existing NAWEC Thermal - GBA | mUS$ | 0.00287 | 0.00034 | 0 | 0 | [6 empty] | 0
Karpower | Existing rented - GBA | mUS$ | 30.3013 | 12.7973 | 0 | 0 | [6 empty] | 0
Brikama III | Committed | mUS$ | 12.9648 | 13.1869 | 8.3526 | 3.1837 | [6 empty] | 2.692
Generator run-time (2022) | [8 empty] | Short run Marginal cost
Power plant | Capacity (MW) | Energy(MWh) | Run time(h) | Marginal cost(US$/MW) | Marginal cost (€/MW) |  |  |  | Power plant | Status | Unit | 2021 | 2022 | 2023 | 2024 | 2025
Brikama I 1 | 5.5 | 550 | 100 | 1.3534 | 1.1504 |  |  |  | Brikama I 1 | Existing NAWEC Thermal - GBA | US$/MWh | 133.06 | 135.34 | 137.71 | 140.07 | 142.52
Brikama I 4 | 5.5 | 40 | 7.2727 | 19.3669 | 16.4618 |  |  |  | Brikama I 4 | Existing NAWEC Thermal - GBA | US$/MWh | 138 | 140.85 | 143.3 | 145.75 | 148.29
Brikama I 7 | 5.5 | 20 | 3.6364 | 37.4935 | 31.8695 |  |  |  | Brikama I 7 | Existing NAWEC Thermal - GBA | US$/MWh | 134 | 136.34 | 138.71 | 141.07 | 143.52
Brikama II 1 | 8.5 | 53610 | 6307.0588 | 0.018016 | 0.015314 |  |  |  | Brikama II 1 | Existing NAWEC Thermal - GBA | US$/MWh | 112 | 113.63 | 115.62 | 117.6 | 119.66
Kotu 4 | 5.5 | 33910 | 6165.4545 | 0.020988 | 0.01784 |  |  |  | Kotu 4 | Existing NAWEC Thermal - GBA | US$/MWh | 127 | 129.4 | 131.69 | 133.98 | 136.35
Kotu 7 | 5 | 10 | 2 | 69.42 | 59.007 |  |  |  | Kotu 7 | Existing NAWEC Thermal - GBA | US$/MWh | 137 | 138.84 | 141.11 | 143.39 | 145.76
Brikama III | 18.4 | 116050 | 6307.0652 | 0.018016 | 0.015314 |  |  |  | Brikama III | Committed | US$/MWh | 112 | 113.63 | 115.62 | 117.6 | 119.66
ICE | 30 | 27810 | 927 | 0.14516 | 0.12338 |  |  |  | ICE | Comitted | US$/MWh | 0 | 134.56 | 137.01 | 139.47 | 142.02
Jambur Solar | 20 | 31890 | 1594.5 | 0 | 0 |  |  |  | Jambur Solar | Comitted | US$/MWh | 0 | 0 | 0 | 0 | 0
Hydro-Imports | 40 | 133510 | 3337.75 | 0.032567 | 0.027682 |  |  |  | Hydro-Imports | Comitted | US$/MWh | 0 | 108.7 | 110.4 | 112.1 | 113.9

## PF_Result
Bus | Readings |  |  |  | Power | received | by | loads | [5 empty] | Loading percentage of the lines |  | Loading percentage on the transformer
| vm_pu | va_degree | p_mw | q_mvar |  | p_mw | q_mvar |  |  | p_mw | q_mvar | va_degree | vm_pu |  |  |  | loading_percent
0 | 1.03 | 0 | 32.4578 | 0 | 0 | 6.333 | 1.1 |  | 0 | 5 | -32.3724 | 0 | 1.03 |  | loading_percent | 0 | 24.4274
1 | 1.03 | 0 | -32 | -24.1495 | 1 | 6.333 | 1.1 |  | 1 | 4.8 | -32.3724 | 0 | 1.03 | 0 | 127.9761 | 1 | 24.4274
2 | 1.0105 | 0.05146 | 14.65 | 4.5 | 2 | 6.333 | 1.1 |  | 2 | 4.89 | -24.4827 | 4.1988 | 1.03 | 1 | 8.8078 | 2 | 24.4274
3 | 1.0107 | 0.51069 | 0 | 0 | 3 | 0.21773 | 0.47 |  | 3 | 5 | -24.4827 | 4.1988 | 1.03 | 2 | 23.5158 | 3 | 24.4274
4 | 0.98313 | 2.6488 | 8.4 | 1.21 | 4 | 3.0482 | 0.27 |  | 4 | 4.89 | -24.4827 | 4.1988 | 1.03 | 3 | 12.1522 | 4 | 24.4274
5 | 1.0125 | 9.0572 | 4.09 | 2.34 | 5 | 7.2068 | 0.67 |  | 5 | 8 | -24.4827 | 4.1988 | 1.03 | 4 | 62.9385 | 5 | 24.4274
6 | 0.98474 | 0.24309 | 2.1 | 1.11 | 6 | 12.4105 | 0.92 |  | 6 | 18.4 | -24.4827 | 4.1988 | 1.03 | 5 | 3.4514 | 6 | 47.1667
7 | 1.0069 | 0.36059 | 0 | 0 | 7 | 5.8787 | 0.29 |  | 7 | 20 |  |  |  | 6 | 0.010153 | 7 | 47.1667
8 | 0.98892 | -0.11965 | 6.11 | -2.71 | 8 | 2.3711 | 0.558 |  | 8 | 40 |  |  |  | 7 | 42.713 | 8 | 47.1667
9 | 0.98893 | -0.11932 | 0 | 0 | 9 | 5.9614 | 0.557 |  |  | 110.98 |  |  |  | 8 | 74.2789 | 9 | 47.1667
10 | 0.96574 | 0.60719 | 6.593 | 1.676 | 10 | 1.3281 | 0.123 | [6 empty] | 9 | 10.2861 | 10 | 47.1667
11 | 0.95404 | -0.81522 | 4.81 | 1.41 | 11 | 4.6942 | 0.438 | [6 empty] | 10 | 15.9845 | 11 | 47.1667
12 | 0.9516 | 0.16488 | 2.85 | 1.82 | 12 | 3.7232 | 1.7 | [6 empty] | 11 | 47.8458 | 12 | 47.1667
13 | 0.9516 | 0.16488 | 0 | 0 | 13 | 5.1819 | 0.64 | [6 empty] | 12 | 127.8677 | 13 | 71.6242
14 | 1.03 | 13.9178 | -54.4 | 1.1196 | 14 | 3.9844 | 1.14 | [6 empty] | 13 | 28.9943 | 14 | 73.5522
15 | 1.0312 | 11.8209 | 0 | 0 | 15 | 1.8071 | -1.53 | [6 empty] | 14 | 34.9472 | 15 | 63.8337
16 | 0.98621 | 3.4846 | 0 | 0 | 16 | 7.5116 | -2.32 | [6 empty] | 15 | 16.7284 | 16 | 65.2628
17 | 0.99026 | 5.8472 | 0 | 0 | 17 | 0.37014 | 0.22 | [6 empty] | 16 | 49.0273 | 17 | 46.9603
18 | 1.0283 | 11.5184 | 0 | 0 | 18 | 2.8087 | 0.74 | [6 empty] | 17 | 3.7954 | 18 | 35.2014
19 | 0.97328 | 2.5087 | 0 | 0 | 19 | 1.3935 | 0.15 | [6 empty] | 18 | 52.8643 | 19 | 35.2014
20 | 0.9758 | 2.5559 | 0 | 0 | 20 | 7.4028 | 1.04 | [6 empty] | 19 | 0.13789 | 20 | 37.0377
21 | 0.98221 | 1.1418 | 0 | 0 | 21 | 6.0964 | 1.1 | [6 empty] | 20 | 0.18312 | 21 | 52.4963
22 | 0.96798 | 1.5702 | 0 | 0 | 22 | 5.4214 | 0.74 | [6 empty] | 21 | 13.2867 | 22 | 35.5353
23 | 0.99078 | 5.9257 | 0 | 0 | 23 | 8.6221 | 0.91 | [6 empty] | 22 | 2.9848 | 23 | 17.0363
24 | 1.0312 | 11.8191 | 0 | 0 | 24 | 4.3546 | 0.71 | [6 empty] | 23 | 0.4114 | 24 | 19.075
25 | 1.0187 | 8.8951 | 0 | 0 | 25 | 2.395 | 0.21 | [6 empty] | 24 | 1.1709 | 25 | 22.1046
26 | 1.0181 | 8.7653 | 0 | 0 | 26 | 3.8103 | 1.61 | [6 empty] | 25 | 11.5265 | 26 | 4.1248
27 | 0.94749 | -0.45724 | 0 | 0 |  | 126.999 | [9 empty] | 27 | 1.7681
28 | 0.98499 | 0.14821 | 0 | 0 | [11 empty] | 28 | 15.7567
29 | 0.98845 | -0.089181 | 0 | 0
30 | 1.0007 | 0.4322 | 0 | 0

## lv_lines (hidden)
| line_name | from_bus | to_bus | length | std_type
0 | LV Line1.1 | Bus LV0 | Bus LV1.1 | 0.08 | NAYY 4x120 SE
1 | LV Line1.2 | Bus LV1.1 | Bus LV1.2 | 0.08 | NAYY 4x120 SE
2 | LV Line1.3 | Bus LV1.2 | Bus LV1.3 | 0.08 | NAYY 4x120 SE
3 | LV Line1.4 | Bus LV1.3 | Bus LV1.4 | 0.08 | NAYY 4x120 SE
4 | LV Line1.5 | Bus LV1.4 | Bus LV1.5 | 0.08 | NAYY 4x120 SE
5 | LV Line2.1 | Bus LV0 | Bus LV2.1 | 0.12 | NAYY 4x120 SE
6 | LV Line2.2 | Bus LV2.1 | Bus LV2.2 | 0.12 | NAYY 4x120 SE
7 | LV Line2.3 | Bus LV2.2 | Bus LV2.3 | 0.12 | NAYY 4x120 SE
8 | LV Line2.4 | Bus LV2.3 | Bus LV2.4 | 0.12 | NAYY 4x120 SE
9 | LV Line2.2.1 | Bus LV2.2 | Bus LV2.2.1 | 0.12 | NAYY 4x120 SE
10 | LV Line2.2.2 | Bus LV2.2.1 | Bus LV2.2.2 | 0.12 | NAYY 4x120 SE